BUILDING MAINTENANCE PLAN

For

Alpha Elementary School 123 Imaginary Lane

Nowhereville, MD 99999

Initial BMP: 8/3/00

1st Return Visit BMP: 12/10/02 2nd Return Visit BMP: 9/3/04

Phone:	301-555-3256	Fax:	301-555-1807

Principal: Jane Doeville Building Service Manager: John McDoe

School No.	7256

INTRODUCTION

Montgomery County Public Schools (MCPS) is committed to addressing indoor environmental problems relating to air quality. A major component of this commitment is the establishment of an IAQ Preventive Maintenance Team. This Team will help to achieve MCPS indoor air quality goals, which are:

To achieve, maintain, and where necessary, to restore an indoor air quality environment in which everyone in a Montgomery County Public Schools (MCPS) facility can perform the necessary tasks of learning, teaching, administering, and sustaining facilities in a safe and healthy manner.

The measures utilized by the team to improve air quality will rely on proactive steps to improve building maintenance and training of staff, rather than responding to complaints. The existing complaint and response process has been retained to ensure that IAQ problems that may arise are handled efficiently and effectively.

Another primary effort of the Team is the initial creation of a building maintenance plan (BMP) specific to this school. This plan is equivalent to a user manual for an automobile. It contains all the necessary routine maintenance schedules, maintenance routines, logs of work orders and repairs, as well as other relevant records. As such, it is a living document that is tailored to the maintenance of the school.

This following BMP is specific for Alpha Elementary School and is designed to be utilized as a tool with the building service manager as the focal user of the tool. Other staff and outside users are expected to contribute to the ongoing growth and accuracy of this living document to ensure its success.

This document, along with the building service procedures manual and the accompanying EPA Tools for Schools kit, are key instruments in maintaining conditions at Alpha Elementary School which would greatly reduce the incidence and severity of indoor air quality concerns. It also provides guidance in addressing issues as they may arise for quick and successful resolution for minimum impact on our primary task of the success of the students and staff of Alpha Elementary School to their full potential.

If you have any questions regarding this living document, its use, or any other environmental and/or safety issues, please do not hesitate to contact your environmental safety coordinator at 301-926-4317.

Thank you,

Richard Hawes, Director

Department of Facilities Management

I

| TABLE OF CONTENTS | Page |
| --- | --- |
| INTRODUCTION | I |
| SECTION 1 General Building Information | 1-1 |
| Building Description | 1-2 |
| Building Information | 1-2 |
| HVAC System Description | 1-2 |
| Relocatable Classroom Log | 1-3 |
| Major Recent Renovations | 1-3 |
| Building Service Personnel Information | 1-4 |
| Building Service Staff Assignments | 1-4 |
| Location of Emergency Equipment and Cut-off Chart | 1-5 |
| SECTION 2 Supply Ventilation Units | 2-1 |
| Supply Units: Type, Brand, Location, and (PM) Preventive Maintenance Routines | 2-2 |
| Supply Unit Preventive Maintenance Routine #1 | 2-4 |
| Supply Unit Preventive Maintenance Routine #2 | 2-5 |
| Supply Unit Preventive Maintenance Routine #4 | 2-6 |
| Supply Unit Preventive Maintenance Routine #5 | 2-7 |
| Lock-Out/Tag-Out of Supply Units | 2-8 |
| Air Filters and Thermostats | 2-10 |
| Supply Unit Service Records | Figure 1 |
| SECTION 3 Exhaust Fans | 3-1 |
| Exhaust Fans: Type, Unit Number, Location, Belt Size, Preventive Maintenance (PM) Routines | 3-2 |
| Exhaust Fan Map | 3-4 |
| Exhaust Fan Preventive Maintenance Routine #1 | 3-5 |
| Exhaust Fan Preventive Maintenance Routine #2 | 3-5 |
| Exhaust Fan Preventive Maintenance Routine #3 | 3-5 |
| Lock-Out/Tag-Out of Exhaust Fans | 3-6 |
| Exhaust Fan Service Records | Figure 2 |
| SECTION 4 Pneumatic System General | 4-2 |
| Air Station: Type, Brand, Location, and Preventive Maintenance Routines | 4-3 |
| Air Station Preventive Maintenance Routine | 4-4 |
| Lock-Out/Tag-Out of Air Station | 4-5 |
| Pneumatic System Service Records | Figure 3 |

SECTION 5 Chiller	5-1

General Description	5-2

Chiller Operation	5-2

General Maintenance	5-2

Chiller Service Record	5-3

| SECTION 6 | Boiler Room | 6-1 |  |
| --- | --- | --- | --- |
|  | Boiler Room Duties | 6-2 |  |
|  | Boiler Room Data | 6-6 |  |
|  | Boiler Room Log Sheets | 6-7 |  |
| SECTION 7 | Building Service Standards Corridor and Entrance Care | 7-1 | 7-2 |
|  | Stairway Care |  | 7-3 |
|  | Office, Lounge, and Health Room Care Classroom Cleaning Restroom Cleaning and Service | 7-5 | 7-4 7-6 |
|  | Kitchen and Cafeteria Services |  | 7-7 |
|  | Outdoor and Grounds Care |  | 7-8 |
|  | Gymnasium Care |  | 7-9 |
| SECTION 8 | Other Maintenance Duties | 8-1 |  |
|  | Ceiling Tile Replacement Procedures | 8-2 |  |
|  | Carpet Care | 8-3 |  |

Appendix A	Requested Maintenance Services	A-1 Procedure for Requesting Maintenance Services		A-2 Record of Maintenance Services		 A-3

| Appendix B | Safety & Environmental Health Guidelines and Recommendations | B-1 |
| --- | --- | --- |
|  | Temperature and Relative Humidity | B-1 |
|  | Carpet Removal Procedures | B-2 |
|  | Lock-Out/Tag-Out | B-4 |
|  | Confined Space | B-5 |
|  | Right-to-Know | B-6 |
|  | Walking/Working Surfaces | B-6 |
|  | Ladders | B-7 |
|  | Sanitization Procedures | B-7 |
|  | Teacher’s Checklist | B-8 |

III

| Appendix C | PM Visit Work Plans Initial Visit Work Plan Primary Responsibility – IAQ Team | C-1 C-2 |
| --- | --- | --- |
|  | Primary Responsibility – Building Service Manager Primary Responsibility – Maintenance Primary Responsibility – Building Staff | C-3 C-4 C-5 |
|  | First Return Visit Work Plan Primary Responsibility – IEQ Team | C-6 |
|  | Primary Responsibility – Building Service Manager Primary Responsibility – Building Staff | C-7 C-8 |
|  | First Return Visit Work Plan Primary Responsibility – IEQ Team | C-9 |
|  | Primary Responsibility – Building Service Manager Primary Responsibility – Building Staff | C-10 C-10 |
| Appendix D | Indoor Environmental Quality (IEQ) Building Reports Follow-up IEQ Assessments | D-1 D-2 |
| Appendix E | Training and Information Hazardous/Toxic Maintenance Chemical Inventory Hazcom Training Program Hazcom Training Record Staff Lock-out/Tag-out Training Lock-Out/Tag-Out Training Program Lock-Out/Tag-Out Training Records | E-1 E-2 E-3 E-9 E-10 E-14 |

Staff IAQ Awareness Training & Tools for Schools Introduction

IAQ Awareness Training Program	E-15

IAQ Awareness Training Records	E-24 MCPS Approved Products List	E-25

IV

SECTION 1	GENERAL BUILDING INFORMATION

This section provides general information on building systems and personnel, and on the building itself.

Page

| Building Description | 1-2 |
| --- | --- |
| Building Information | 1-2 |
| HVAC System Description | 1-2 |
| Relocatable Classroom Log | 1-3 |
| Major Recent Renovations | 1-3 |
| Building Service Personnel Information | 1-4 |
| Building Service Staff Assignments | 1-4 |
| Location of Emergency Equipment and Cut-off Chart | 1-5 |
| Component List for Alpha Elementary (12/7/99) | Figure 1 |

1-1

BUILDING DESCRIPTION

Alpha Elementary is a split-level, slab-on-grade facility containing 30 classrooms, a multi- purpose room, gym, IMC, administrative offices, two resource rooms, one math lab, one speech room, and two reading initiative rooms.

Substantial additions and/or modernizations to the original building (opened 1965) occurred in 1992.

Most of the roof is built-up asphalt. Some areas of the roof are pitched shingled.

BUILDING INFORMATION

| Grades served: | K-5 |
| --- | --- |
| Enrollment (2004): | 650 |
| School Capacity: | 678 |
| Original Construction: | 1965 |
| Last Modernization: | 1992 |
| Site Size: | 9.9 acres |
| Square Footage: | 68,755 |

HVAC SYSTEM DESCRIPTION

Two gas-fired low-pressure fire tube type boilers heat the building. The two-pipe-system distributes heater water to unit ventilators/fan coil units located in classrooms and offices. The temperature of the main heating loop for the building is controlled by Energy Management. Classroom temperature is controlled by individual thermostats. The pneumatic air station located in the boiler room sends a supply pressure of (15 psi in winter and 20 psi in summer) to all thermostats for proper operation.

The kindergarten rooms K1 and K2 have individual air handlers. Energy Management controls the kindergarten temperature by operating the 3-way valve for the air handler. The administrative offices, health room, media center, and computer lab have roof-top units for heating and cooling. Those units are controlled by Energy Management.

Building-wide cooling is by an air cooled chiller except for DX cooling in the following zones: 1, 3, 4, 6, 7, & 8. The chilled water is distributed to each classroom unit ventilator/fan coil unit.

Ventilation air is connected to the Andover Energy Management System that controls the starting/stopping of the HVAC systems at the beginning and end of each occupancy period. The HVAC equipment is operated from the thermostat controls within the building during the occupied period. Roof-top units and air handlers are controlled by energy management.

1-2

Relocatable Classroom Log

| Room Number | Mfr. Serial Number | MCPS Serial Number | Manufacture | Age (yrs) | Leased/ Owned |
| --- | --- | --- | --- | --- | --- |
| NONE | NONE | NONE | NONE |  |  |

Major Recent Renovations

No major renovations have been completed at Alpha Elementary since FY-97.

1-3

BUILDING SERVICE PERSONNEL INFORMATION

School:		Principal’s Phone #:

Building Service Manager 	 Phone #:

Building Service Leader 	 Phone #:

Plant Equipment Operator 	 Phone #:

Building Service Supervisor 	 Phone #:

BUILDING SERVICE STAFF ASSIGNMENTS

| FIRST SHIFT | SECOND SHIFT | SPECIAL SHIFT |
| --- | --- | --- |
| Working Hours |  |  |
| Number Of Staff |  |  |

| Name | Phone Number | Shift | Training* |
| --- | --- | --- | --- |

*1 = Asbestos Awareness, 2 = Right-to-Know Law, 3 = Basic Training, 4 = Boiler Operation, 5 = Plant Equipment Operation, 6 = Refresher, 7 = Air Conditioning, 8 = Supervisory and Leadership Skills, 9 = Sexual Harassment, and 10 = Bloodborne Pathogens

1-4

LOCATION OF EMERGENCY EQUIPMENT AND CUT-OFF CHART

The attached color-coded floor plan according to the key below should show the locations of fire extinguishers, emergency generator, main cut-off valves and switches, for each facility should be posted in the building service manager’s office and in the boiler room. Anyone with access to the chart should be able to respond to a problem involving any of the identified items quickly and effectively.

EMERGENCY CUT OFF CHART

+	= Main Water Location #	 = Fire Extinguishers

<	= Generator

>	= Main Electric

=	= Natural Gas Cut-Off

/	= Main Oil Line

1-5

In actual BMPs, a floor plan is inserted here with emergency equipment/cut-off locations.

SECTION 2	SUPPLY VENTILATION UNITS

This section provides specific information on the ventilation systems regarding their type, brand, location, and preventative maintenance routine. These routines are schedules of tasks to be performed by building service and maintenance staff to ensure proper operation and cleanliness as the first step in a healthful learning environment.

Page

Supply Units: Type, Brand, Location, and

Preventive Maintenance Routines	2-2

Supply Unit Preventive Maintenance Routine #1	2-4

Supply Unit Preventive Maintenance Routine #2	2-5

Supply Unit Preventive Maintenance Routine #4	2-6

Supply Unit Preventive Maintenance Routine #5	2-7

Lock-out/Tag-out of Supply Units	2-8

Air Filters and Thermostats	2-10

Supply Unit Service Records*	Figure 1

*These records are for each piece of ventilation equipment and are to be utilized by any and all personnel who may perform maintenance on this equipment.

2-1

SUPPLY VENTILATION UNITS

TYPE, BRAND, LOCATION, PREVENTIVE MAINTENANCE (PM) ROUTINES

The spreadsheet on the following page allows you to cross-reference the appropriate preventative maintenance routine for each type of supply ventilation unit in this facility.

2-2

| Supply Ventilation Equipment – Preventive Maintenance |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Building: Alpha ES Date of Assessment: June 2004 |  |  |  |  |  |  |  |  |
| Unit Location | Area/Zone Served | Unit Type | Brand | Model | Serial No. | Direct Drive | Belt | PM Routine |
| Under window | Staff lounge | Unit ventilator | Nelson Aire | FE126B | T67Ax | Yes |  | 1 |
| Under window | IMC Office | Unit ventilator | Engineered Air | VUV-16 | RV255 | Yes |  | 1 |
| Mechanical Room #1 | IMC | AHU | Engineered Air | AHU-8 |  | Yes |  | 2 |
| Under window | Kitchen | Fan coil unit | Nelson Aire | FE125C | P88Tv | Yes |  | 1 |
| Under window | Principal’s Office | Unit ventilator | Trane | FCBB06055 | V99H990 | Yes |  | 1 |
| Roof penthouse | APR | AHU | York | K3ET9900 | NHT67888 | No | 4L38 0 | 2 |
| Under window | Room 1 | Unit ventilator | Engineered Air | VUV-16 | RV255 | Yes |  | 1 |
| Under window | Room 2 | Unit ventilator | Engineered Air | VUV-16 | RV255 | Yes |  | 1 |
| Under window | Room 3 | Unit ventilator | Engineered Air | VUV-16 | RV255 | Yes |  | 1 |
| Under window | Room 4 | Unit ventilator | Engineered Air | VUV-16 | RV255 | Yes |  | 1 |
| Under window | Room 5 | Unit ventilator | Engineered Air | VUV-16 | RV255 | Yes |  | 1 |
| Under window | Room 6 | Unit ventilator | Engineered Air | VUV-16 | RV255 | Yes |  | 1 |
| Under window | Room 7 | Unit ventilator | Engineered Air | VUV-16 | RV255 | Yes |  | 1 |
| Under window | Room 8 | Unit ventilator | Engineered Air | VUV-16 | RV255 | Yes |  | 1 |

The number of supply ventilation units at MCPS schools is variable, ranging from less than 20 to over 200.

# SUPPLY UNIT PREVENTIVE MAINTENANCE ROUTINE #1

(Unit ventilators, Fan coil units)

| RESPONSIBILITY | TASK | Every Month | Every 3 Months | Every 6 Months | Every Return Visit |
| --- | --- | --- | --- | --- | --- |
| BSM | Check filter condition | X |  |  |  |
| BSM | Check and clear area in front of intake grill | X |  |  |  |
| BSM | Change filter. Verify thermostat guard is in place. Check for pneumatic and water leaks. Check damper operation |  | X |  |  |
| BSM | Replace filter, remove debris, vacuum and wipe interior (including coils), clean accessible side of coil, clean and sanitize pan, oil bearings, check thermostat operation, oil motor if needed, check valve operation, flush condensate line with clean water, check water valve for exterior leakage |  |  | X |  |
| Maintenance | Check damper calibrations, calibrate thermostats, inspect electrical connections, blow out condensate lines |  |  | As Needed |  |
| IEQ Team | Check damper calibrations, calibrate thermostats, inspect electrical connections, blow out condensate lines |  |  |  | X |

2-4

# SUPPLY UNIT PREVENTIVE MAINTENANCE ROUTINE #2

(Portable classroom units, heat pumps, central air handling units, rooftop units)

| RESPONSIBILITY | TASK | Every Month | Every 3 Months | Every 6 Months | Every Return Visit |
| --- | --- | --- | --- | --- | --- |
| BSM or PEO | Check filter condition | X |  |  |  |
| BSM or PEO | Change filter. |  | X |  |  |
| BSM or PEO | Vacuum interior of unit |  |  | X |  |
| Maintenance | Check damper calibrations, calibrate thermostats, inspect electrical connections |  |  | As Needed |  |
| IEQ Team | Check damper calibrations, calibrate thermostats, inspect electrical connections |  |  |  | X |

2-5

# SUPPLY UNIT PREVENTIVE MAINTENANCE ROUTINE #4

(Condensers)

| RESPONSIBILITY | TASK | Every Month | Every 3 Months | Every 6 Months | Every Return Visit |
| --- | --- | --- | --- | --- | --- |
| IEQ Team | Remove corrosion from unit surfaces and repaint. Inspect refrigerant piping and fittings for leaks. Check fan assemblies for loose sheaves, excessive end play, abnormal vibration and noise. Determine if lubrication of fan bearings is needed; lubricate with proper material (e.g. non- detergent SAE 30 oil, grease, etc.) Do not over lubricate. Chemically clean coil and straighten coil fins. Inspect control panel and disconnect wiring to ensure all connections are tight, insulation is intact, and that no water damage is evident. Remove accumulated dust and dirt from control panel. Check unit operating pressures, super heat and subcooling. Record readings on work sheet in this section. |  |  |  | X |

2-6

# SUPPLY UNIT PREVENTIVE MAINTENANCE ROUTINE #5

(Baseboard heaters)

| RESPONSIBILITY | TASK | Every Month | Every 3 Months | Every 6 Months | Every Return Visit |
| --- | --- | --- | --- | --- | --- |
| BSM or PEO | Vacuum fins and visually inspect connections and housing for damage | X |  |  |  |
| IEQ Team | Check thermostat operation/calibration |  |  |  | X |

2-7

LOCK-OUT/TAG-OUT OF SUPPLY VENTILATION UNITS

The following steps need to be completed when servicing air handlers. This is to remove sources of energy, which may cause harm if accidentally released during servicing. This procedure is called “Lock- Out/Tag-Out”: It must be performed in accordance with a written Hazardous Energy Control Program.

- Identify circuit breaker that supplies unit to be de-energized.

- Flip breaker to the off position.

- Verify that no power is present at the unit. Flip switch at unit on and off and verify unit is off; check line voltage incase power is supplied by secondary source.

- After it has been verified that no power is present at the unit, place appropriate lock on breaker. Secure breaker lock with padlock. Key for padlock must be kept with individual working on unit. Place label on breaker lock indicating who has key to lock.

- To energize unit, turn unit switch to off position. Verify that all tools, etc. have been removed from unit and mechanisms are secure

- Unlock breaker padlock and remove breaker lock.

- Flip breaker to on position.

- Turn unit switch to on position and verify it is operating correctly

The spread sheet on the following page lists circuit breaker locations for supply ventilation units.

2-8

| Supply Ventilation Equipment – Electrical Lock-Out/Tag-out |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Building: Alpha ES Date of Assessment: June 2004 |  |  |  |  |  |  |
| ALWAYS RE-VERIFY BREAKER INFORMATION BEFORE WORKING ON UNITS! |  |  |  |  |  |  |
| Unit Location | Area/Zone Served | Unit Type | Voltage | Breaker Panel | Panel Location | Breaker |
| Under window | Staff lounge | Unit ventilator | 115 | H | Boiler Room | 20 |
| Under window | IMC Office | Unit ventilator | 115 | E3 | Hall across art room | 12 |
| Mechanical Room #1 | IMC | AHU | 480 3ph | E3 | Hall across art room | 31,33,35 |
| Under window | Kitchen | Fan coil unit | 115 | K | Hall across kitchen | 18 |
| Under window | Principal’s Office | Unit ventilator | 115 | H | Boiler Room | 26 |
| Roof penthouse | APR | AHU | 480 3ph | E1 | Closet across room 5 | 16,18,20 |
| Under window | Room 1 | Unit ventilator | 115 | MDP | Closet by BSM office | 15 |
| Under window | Room 2 | Unit ventilator | 115 | MDP | Closet by BSM office | 15 |
| Under window | Room 3 | Unit ventilator | 115 | MDP | Closet by BSM office | 10 |
| Under window | Room 4 | Unit ventilator | 115 | MDP | Closet by BSM office | 10 |
| Under window | Room 5 | Unit ventilator | 115 | MDP | Closet by BSM office | 12 |
| Under window | Room 6 | Unit ventilator | 115 | T5 | Closet by room 9 | 6 |
| Under window | Room 7 | Unit ventilator | 115 | T5 | Closet by room 9 | 6 |
| Under window | Room 8 | Unit ventilator | 115 | L6 | Boiler Room | 10 |

The number of supply ventilation units at MCPS schools is variable, ranging from less than 20 to over 200.

## AIR FILTERS and THERMOSTATS

The spreadsheet on the following page lists air filters used for each supply unit.

2-10

| Supply Ventilation Equipment – Air Filters and Thermostats |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Building: Alpha ES Date of Assessment: June 2004 |  |  |  |  |  |  |  |
| Unit Location | Area/Zone Served | Unit Type | Brand | Filter Size (in.) | Filter Type | Stat Brand | Stat Model |
| Under window | Staff lounge | Unit ventilator | Nelson Aire | 11.5 x 33.5 x 1 | Roll media |  |  |
| Under window | IMC Office | Unit ventilator | Engineered Air | 14 x 32 x 1 | Roll media | Barber Coleman | TK-1741 |
| Mechanical Room #1 | IMC | AHU | Engineered Air | 20 x 33 x 2 | Roll media | Barber Coleman | TK-1741 |
| Under window | Kitchen | Fan coil unit | Nelson Aire | 8.5 x 25 x 1 | Roll media | Robert Shaw | T33-301 |
| Under window | Principal’s Office | Unit ventilator | Trane | 14.5 x 18.5 x 1 (2) | Disposable |  | Integral |
| Roof penthouse | APR | AHU | York | 16 x 40 x 1 (2) | Tri-Link | Barber Coleman | TK-1741 |
| Under window | Room 1 | Unit ventilator | Engineered Air | 14 x 32 x 1 | Roll media | Barber Coleman | TK-1741 |
| Under window | Room 2 | Unit ventilator | Engineered Air | 14 x 32 x 1 | Roll media | Barber Coleman | TK-1741 |
| Under window | Room 3 | Unit ventilator | Engineered Air | 14 x 32 x 1 | Roll media | Barber Coleman | TK-1741 |
| Under window | Room 4 | Unit ventilator | Engineered Air | 14 x 32 x 1 | Roll media | Barber Coleman | TK-1741 |
| Under window | Room 5 | Unit ventilator | Engineered Air | 14 x 32 x 1 | Roll media | Barber Coleman | TK-1741 |
| Under window | Room 6 | Unit ventilator | Engineered Air | 14 x 32 x 1 | Roll media | Barber Coleman | TK-1741 |
| Under window | Room 7 | Unit ventilator | Engineered Air | 14 x 32 x 1 | Roll media | Barber Coleman | TK-1741 |
| Under window | Room 8 | Unit ventilator | Engineered Air | 14 x 32 x 1 | Roll media | Barber Coleman | TK-1741 |

## The number of supply ventilation units at MCPS schools is variable, ranging from less than 20 to over 200.

| Supply Ventilation PM Log Sheet – ALPHA ES |  |  |  | Month: |  |
| --- | --- | --- | --- | --- | --- |
| Sheet Completed by: |  |  |  | Year: |  |
| Unit Location | Area Served | Unit Type | Filter Changed | Unit Cleaned | Needs Repair |
| Under window | Staff lounge | Unit ventilator |  |  |  |
| Under window | IMC Office | Unit ventilator |  |  |  |
| Mechanical Rm #1 | IMC | AHU |  |  |  |
| Under window | Kitchen | Fan coil unit |  |  |  |
| Under window | Principal’s Office | Unit ventilator |  |  |  |
| Roof penthouse | APR | AHU |  |  |  |
| Under window | Room 1 | Unit ventilator |  |  |  |
| Under window | Room 2 | Unit ventilator |  |  |  |
| Under window | Room 3 | Unit ventilator |  |  |  |
| Under window | Room 4 | Unit ventilator |  |  |  |
| Under window | Room 5 | Unit ventilator |  |  |  |
| Under window | Room 6 | Unit ventilator |  |  |  |
| Under window | Room 7 | Unit ventilator |  |  |  |
| Under window | Room 8 | Unit ventilator |  |  |  |
| Comments (if repairs needed, describe here): |  |  |  |  |  |

SECTION 3	EXHAUST FANS

This section provides specific information on the building exhaust systems regarding their type, number, location, belt size, and preventative maintenance routine. These routines are schedules of tasks to be performed by building service and maintenance staff to ensure proper operation as the first step in a healthful learning environment.

Page

Exhaust Fans: Type Unit Number, Location,

Belt Size, and Preventive Maintenance (PM) Routines	3-2

Exhaust Fan Map	3-4

Exhaust Fan Preventive Maintenance Routine #1	3-5

Exhaust Fan Preventive Maintenance Routine #2	3-5

Exhaust Fan Preventive Maintenance Routine #3	3-5

Lock-Out/Tag-Out of Exhaust Fans	3-6

Exhaust Fan Service Records	Figure 2

3-1

EXHAUST FANS TYPE, UNIT NUMBER, LOCATION, BELT SIZE, PREVENTIVE MAINTENANCE (PM) ROUTINE

The spreadsheet on the following page allows you to cross-reference the appropriate preventive maintenance routine for each type of exhaust fan found at this facility.

3-2

| Exhaust Ventilation Equipment – Preventive Maintenance |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Building: Alpha ES Date of Assessment: June 2004 |  |  |  |  |  |  |  |  |  |
| Fan | Location | Area/Zone Served | Unit Type | Brand | Model | Serial No. | Direct Drive | Belt | PM Routine |
| 1 | Roof above staff lounge | Staff Lounge | Exhaust fan | Dayton | CI 14B | 222RT | Yes |  | 2 |
| 2 | Roof above APR | APR | Exhaust fan | Greenheck | TX265 | 26133 | Yes |  | 2 |
| 3 | Roof above hall by rm 11 | Rooms 11,12,13,14 | Exhaust fan | Power | LC30BC | 18555 | No | A75 | 1 |
| 4 | Roof above BSM Office | Girls’ restrm by BSM Office | Exhaust fan | Power | LC30BC | 18559 | No | A75 | 1 |
| 5 | Roof above boys’ restrm | Boys’ restrm by BSM Office | Exhaust fan | Greenheck | CX299 | 22TY6 | Yes |  | 2 |
| 6 | Roof above hall by room 3 | Rooms 3,4,5,6 | Exhaust fan | Greenheck | CX299 | 22TY7 | Yes |  | 2 |
| 7 | Roof near room 17 | Restrooms by room 17 | Exhaust fan | Greenheck | CX299 | 22TY8 | Yes |  | 2 |
| 8 | Roof near room 19 | Restrooms by room 19 | Exhaust fan | Chelsea | RDD90XB | 55616 | Yes |  | 2 |
| K | Roof above kitchen | Kitchen (removed from svc) | Exhaust fan | Chelsea | RDD90XB | 55615 | Yes |  | None |

In actual BMPs, a school map with marked exhaust fan locations is inserted here.

3-4

EXHAUST FAN PREVENTIVE MAINTENANCE (PM) ROUTINE #1

| RESPONSIBILITY | TASK | Every Month | Every 3 Months | Every 6 Months |
| --- | --- | --- | --- | --- |
| BSM | Inspect motor and belt |  | X |  |
|  | Oil/grease, if applicable |  |  |  |
|  | Clean housing and fan, check operation and secure top |  |  |  |

EXHAUST FAN PREVENTIVE MAINTENANCE ROUTINE #2

| RESPONSIBILITY | TASK | Every Month | Every 3 Months | Every 6 Months |
| --- | --- | --- | --- | --- |
| BSM | Inspect motor |  | X |  |
|  | Oil/grease, if applicable |  |  |  |
|  | Clean housing and fan, check operation and secure top |  |  |  |

EXHAUST FAN PREVENTIVE MAINTENANCE ROUTINE #3

| RESPONSIBILITY | TASK | Every Month | Every 3 Months | Every 6 Months |
| --- | --- | --- | --- | --- |
| BSM | Inspect motor and belt | X |  |  |
|  | Oil/grease, if applicable |  |  |  |
|  | Clean housing and fan, check operation and secure top |  |  |  |

3-5

LOCK-OUT/TAG-OUT OF EXHAUST FANS

The following steps need to be completed when servicing exhaust fans. This is to remove sources of energy, which may cause harm if accidentally released during servicing. This procedure is called “Lock- Out/Tag-Out”: It must be performed in accordance with a written Hazardous Energy Control Program.

- Identify circuit breaker that supplies unit to be de-energized.

- Flip breaker to the off position.

- Verify that no power is present at the unit. Flip switch at unit on and off and verify unit is off; check line voltage incase power is supplied by secondary source.

- After it has been verified that no power is present at the unit, place appropriate lock on breaker. Secure breaker lock with padlock. Key for padlock must be kept with individual working on unit. Place label on breaker lock indicating who has key to lock.

- To energize unit, turn unit switch to off position. Verify that all tools, etc. have been removed from unit and mechanisms are secure

- Unlock breaker padlock and remove breaker lock.

- Flip breaker to on position.

- Turn unit switch to on position and verify it is operating correctly

The spreadsheet on the following page lists circuit breaker locations for exhaust fans.

3-6

| Exhaust Ventilation Equipment – Electrical Lock-out/Tag-out |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Building: Alpha ES Date of Assessment: June 2004 |  |  |  |  |  |  |  |  |  |
| ALWAYS RE-VERIFY BREAKER INFORMATION BEFORE WORKING ON UNITS! |  |  |  |  |  |  |  |  |  |
| Fan | Location | Area/Zone Served | Unit Type | Voltage | Fan Control | Starter | Breaker Panel | Panel Location | Breaker |
| 1 | Roof above staff lounge | Staff Lounge | Exhaust fan | 115/1/60 | Wall switch |  | B | Across staff restrms | 11 |
| 2 | Roof above APR | APR | Exhaust fan | 115/1/60 | Humidistat |  | B | Across staff restrms | 17 |
| 3 | Roof above hall by rm 11 | Rooms 11,12,13,14 | Exhaust fan | 120/1/60 | Humidistat |  | D | Hall by room 13 | 20 |
| 4 | Roof above BSM Office | Girls’ restrm by BSM Office | Exhaust fan | 120/1/60 | Humidistat |  | A | Hall by room 5 | 21 |
| 5 | Roof above boys’ restrm | Boys’ restrm by BSM Office | Exhaust fan | 115/1/60 | Wall switch |  | C | Hall by APR | 1 |
| 6 | Roof above hall by room 3 | Rooms 3,4,5,6 | Exhaust fan | 115/1/60 | Wall switch |  | C | Hall by APR | 1 |
| 7 | Roof near room 17 | Restrooms by room 17 | Exhaust fan | 115/1/60 | Wall switch |  | F | Hall by room 17 | 11 |
| 8 | Roof near room 19 | Restrooms by room 19 | Exhaust fan | 120/1/60 | Wall switch |  | F | Hall by room 17 | 11 |
| K | Roof above kitchen | Kitchen (removed from svc) | Exhaust fan | 120/1/60 |  |  |  |  |  |

| Exhaust Ventilation PM Log Sheet – ALPHA ES |  |  |  | Month: |  |
| --- | --- | --- | --- | --- | --- |
| Sheet Completed by: |  |  |  | Year: |  |
| Fan | Unit Location | Area Served | Cleaned/oiled | New belt | Needs Repair |
| 1 | Roof above staff lounge | Staff Lounge |  |  |  |
| 2 | Roof above APR | APR |  |  |  |
| 3 | Roof above hall by rm 11 | Rooms 11,12,13,14 |  |  |  |
| 4 | Roof above BSM Office | Girls’ restrm by BSM Office |  |  |  |
| 5 | Roof above boys’ restrm | Boys’ restrm by BSM Office |  |  |  |
| 6 | Roof above hall by room 3 | Rooms 3,4,5,6 |  |  |  |
| 7 | Roof near room 17 | Restrooms by room 17 |  |  |  |
| 8 | Roof near room 19 | Restrooms by room 19 |  |  |  |
| Comments (if repairs needed, describe here): |  |  |  |  |  |

SECTION 4	PNEUMATIC SYSTEM

This section provides specific information on the pneumatic system; the type, brand, location, and preventative maintenance routine is included. These routines are schedules of tasks to be performed by building service and maintenance staff.

Page

General	4-2

Air Station: Type, Brand, Location, and

Preventive Maintenance (PM) Routine	4-3

Air Station Preventive Maintenance Routine	4-4

Lock-Out/Tag-Out of Air Station	4-5

Pneumatic System Service Records	Figure 3

4-1

GENERAL

A central air compressor usually supplies compressed air for pneumatic control systems. Air in the system must be clean and dry; pressure is reduced to 15-18 psi depending on pneumatic system age.

Intake air is passed through a screen filter. Compressed air is passed through a check valve and then an oil filter.

Standard high-pressure air from the compressor is passed through a pressure-reducing valve (prv) where its final system pressure is adjusted to 15-18 psi.

4-2

AIR STATION

TYPE, BRAND, LOCATION, PREVENTIVE MAINTENANCE (PM) ROUTINES

The spreadsheet on the following page allows you to cross-reference the appropriate preventative maintenance routine for each pneumatic system air station found in this facility.

4-3

| Pneumatic System--Preventive Maintenance |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Building: ALPHA ELEMENTARY SCHOOL |  |  |  |  |  |  |
| Date of Assessment: JUNE 2004 |  |  |  |  |  |  |
| Type of Unit | Unit Location | Brand | Model | Serial # | Direct Drive | Belt Size |
| Compressor | Boiler Room | Quincy | 2100RB | 61292L5 | No | B52 |
| Air Dryer | Boiler Room | Hankison | 8010 | 0302L-8504 | Yes |  |

AIR STATION PREVENTIVE MAINTENANCE ROUTINE

| RESPONSIBILITY | TASK | Every Week | Every Month | Every 6 Months | Every Return Visit |
| --- | --- | --- | --- | --- | --- |
| BSM | Drain compressor tank, filter bowl, and any air lines that have drain cocks. Check compressor crankcase oil level. Check compressor safety-relief valve | X |  |  |  |
| Maintenance | Change crankcase oil. Check compressor pressure switches. Inspect for moisture, oil, or dirt in the air lines. Inspect starter or starting switch. Clean contacts if necessary. Measure motor current, compare with full load rating and overload heater size. |  |  | X |  |
| BSM | Oil the compressor motor(s). Check pressure relief valve and the check valve. Check operation of air drier. Check for moisture, oil, and dirt in air lines. Clean air intake filter, felt, and screens. Check compressor belt(s). |  |  | X |  |
| IEQ Team | Inspect all steel fittings for rust and replace if needed. Replace cartridge-type intake air filter |  |  |  | X |

4-4

LOCK-OUT/TAG-OUT OF AIR STATION COMPONENTS

The following steps need to be completed when servicing the compressors or air dryer. This is to remove sources of energy, which may cause harm if accidentally released during servicing. This procedure is called “Lock-Out/Tag-Out”: It must be performed in accordance with a written Hazardous Energy Control Program.

- Identify circuit breaker that supplies unit to be de-energized.

- Flip breaker to the off position.

- Verify that no power is present at the unit. Flip switch at unit on and off and verify unit is off; check line voltage incase power is supplied by secondary source. - After it has been verified that no power is present at the unit, place appropriate lock on breaker.

Secure breaker lock with padlock. Key for padlock must be kept with individual working on unit. Place label on breaker lock indicating who has key to lock. - To energize unit, turn unit switch to off position. Verify that all tools, etc. have been removed from unit and mechanisms are secure - Unlock breaker padlock and remove breaker lock.

- Flip breaker to on position. - Turn unit switch to on position and verify it is operating correctly The spreadsheet on the following page lists circuit breaker locations for air station components.

4-5

| Pneumatic System—Electrical Lock-out/Tag-out |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Building: ALPHA ELEMENTARY SCHOOL |  |  |  |  |  |  |  |
| Date of Assessment: JUNE 2004 |  |  |  |  |  |  |  |
| ALWAYS RE-VERIFY BREAKER INFORMATION BEFORE WORKING ON UNIT! |  |  |  |  |  |  |  |
| Type of Unit | Unit Location | Brand | Model | Voltage | Breaker Panel | Panel Location | Breaker |
| Compressor | Boiler Room | Quincy | 2100RB | 208/3/60 | M | Boiler Room | 21 |
| Air Dryer | Boiler Room | Hankison | 8010 | 115/1/60 | M | Boiler Room | 22 |

AIR STATION SERVICE RECORDS FOR 	 in 	 Page 	 of

| NAME | DATE | WEEKLY | MONTHLY | 6 MONTH | 12 MONTH | COMMENTS |
| --- | --- | --- | --- | --- | --- | --- |

SECTION 5	CHILLER

This section provides information and service records for the school’s chiller.

|  | Page |
| --- | --- |
| General Description | 5-2 |
| Chiller Operation | 5-2 |
| General Maintenance | 5-2 |
| Chiller Service Record | 5-3 |

5-1

CHILLER

General Description

Type of Unit: 2 Trane (#CG101) Air Cooled Reciprocating (R-22 refrigerant) chiller

Size: 100 tons each

Chiller Operation

The chiller is operated only when the building is occupied. It is cycled automatically with temperature sensors in the return water from the building. The chilled water temperature is set at 450F. The unit is started 1 hour before building occupancy to bring space temperatures to an acceptable level. The unit is operated for cooling purposes and provides some dehumidification capability. The chilled water circulation pump is to be operated whenever the chiller operates.

General Maintenance The Division of Maintenance performs all maintenance of the chiller system. The Building Service Manager is required to keep the area around the chiller clear of debris on an as need basis. During summer operations, the Building Service Manager must confirm and record temperature of chiller water, water conditions and check for unusual noises on a daily basis. A form for recording those activities follows.

5-2

CHILLER SERVICE RECORD

The form is to be used by the building service manager during the cooling season on a daily basis.

| Date | Water Temperature | Name | Time and Comments |
| --- | --- | --- | --- |

5-3

SECTION 6	BOILER ROOM

This section provides information regarding the boiler room and its equipment including proper operating values, duties, and appropriate log sheets.

Page

Boiler Room Duties	6-2

Boiler Room Data	6-6

Boiler Room Log Sheets	6-7

6-1

BOILER ROOM DUTIES

Routine maintenance tasks for the boiler room as outlined in the MCPS Procedure Manual from the Division of School Plant Operations are listed on the following pages with appropriate scheduling.

6-2

| BOILER ROOM DUTIES | HOURLY | DAILY | WEEKLY | MONTHLY | QUARTERLY | AS REQUIRED |
| --- | --- | --- | --- | --- | --- | --- |
| Check burner operation | X |  |  |  |  |  |
| Check gauge readings | X |  |  |  |  |  |
| Check for leaks | X |  |  |  |  |  |
| Blow down low water cut-offs * |  | X |  |  |  |  |
| Test try cocks * |  | X |  |  |  |  |
| Blow down water columns * |  | X |  |  |  |  |
| Test glass gauges * |  | X |  |  |  |  |
| Blow down boilers * |  | X |  |  |  |  |
| Test safety valves * |  |  | X |  |  |  |
| Test relief valves |  |  |  | X |  |  |
| Service oil burners # |  | +X |  |  |  | X |
| Stick fuel oil storage tank |  | X |  |  |  |  |
| Clean fuel oil strainers |  |  | #X |  |  | X |
| Test emergency switch |  |  |  |  | X |  |
| Check fresh air louvers |  |  | X |  |  |  |
| Lubricate motors & equipment |  |  |  |  |  | X |
| Tighten bolts, screws, etc. |  |  |  | X |  | X |
| Clean boilers (fire side) @ |  |  |  | #X |  | X |
| Sweep boiler room floor |  |  | X |  |  |  |
| Dust tops of boilers and pipes |  |  |  | X |  |  |
| Clean boiler room equipment |  |  |  | X |  |  |
| Clean dial faces, glass gauges |  |  |  | X |  |  |
| Remove trash, rags, etc. |  | X |  |  |  |  |
| Clean boiler room (thoroughly) |  |  |  | X |  |  |
| Replace burned out light bulbs |  |  |  |  |  | X |

Steam boilers *	Rotary cup burners +

Heavy oil burners #	PEOs only @

6-3

| BOILER ROOM DUTIES (cont’d) | HOURLY | DAILY | WEEKLY | MONTHLY | QUARTERLY | AS REQUIRED |
| --- | --- | --- | --- | --- | --- | --- |
| Clean up spilled oil |  |  |  |  |  | X |
| Check air compressor operation |  | X |  |  |  |  |
| Drain air compressor tank |  |  | X |  |  | X |
| Drain filter bowls and separator |  |  | X |  |  |  |
| Check oil level in compressor |  |  | X |  |  |  |
| Test compressor relief valve |  |  | X |  |  |  |
| Check dryer operation |  | X |  |  |  |  |
| Clean/replace air intake filter |  |  |  | X |  | X |
| Check circulator pumps |  | X |  |  |  |  |
| Check condensate receivers * |  | X |  |  |  |  |
| Check automatic water feeders |  | X |  |  |  |  |
| Check water heater |  | X |  |  |  |  |
| Test water heater relief valve |  |  |  |  | X |  |
| Check sump pumps |  | X |  |  |  |  |
| Check fuel oil pumps |  | X |  |  |  |  |
| Check belt condition / tension |  |  | X |  |  |  |
| Replace guards / covers |  | X |  |  |  | X |
| Exercise gate valves |  |  |  |  | X |  |
| Check for damaged insulation |  |  |  | X |  |  |
| Check boiler alarm |  | X |  |  |  |  |
| Check AHUs and unit ventilators |  | X |  |  |  |  |
| Service AHUs and unit ventilators |  |  |  |  |  | X |
| Check filters – replace |  |  |  | X | X | X |
| Check thermostats and controls @ |  |  |  |  | X | X |

| Steam boilers * | Rotary cup burners | + |
| --- | --- | --- |
|  |  | 6-4 |

| BOILER ROOM DUTIES (cont’d) | HOURLY | DAILY | WEEKLY | MONTHLY | QUARTERLY | AS REQUIRED |
| --- | --- | --- | --- | --- | --- | --- |
| Check A/C chillers | X |  |  |  |  |  |
| Check A/C cooling towers | X |  |  |  |  |  |
| Read A/C gauges and record on log | X |  |  |  |  | X |
| Service emergency generator |  |  | X |  |  |  |
| Check emergency light packs |  |  |  |  | X |  |
| Test fire alarm system |  | X |  |  |  |  |
| Maintain log sheets |  | X |  |  |  |  |
| Maintain service record cards |  |  |  |  |  | X |
| Check stock of service supplies |  |  |  | X |  |  |
| Paint boiler room / pipes @ |  |  |  |  | X |  |
| Paint equipment @ |  |  |  |  | X |  |
| Maintain tools and equipment |  | X |  |  | X |  |

Steam boilers *	Rotary cup burners +

Heavy oil burners #	PEOs only @

6-5

BOILER ROOM DATA

Write N/A in the spaces which do not apply to this system. Place this data sheet in a protective holder and display it in a conspicuous place in the boiler room.

Steam 		Hot Water 		Steam Conversion Hot Water

Boiler cut in 	 ˚F or psi			Boiler cut out 		 ˚F or psi Fuel oil – grade number 		tank capacity 	 gallons

Oil temperature – from fuel tank 		 ˚F	at burner 	 ˚F Oil pressure – at pump 	 psi	at burner 	 psi

Oil pressure – suction side of pump 	 inches Hg Side arm oil heater in use 	 yes/no

Air atomizing oil burner (air pressure)

Low fire 	 psi	High fire 	 psi Natural gas burners (gas pressure)

Supply 	 inches wc	Reduced 	 inches wc Water pressure (hot water heating systems) – boiler 	 psi

Pump supply 	 psi	Pump discharge 	 psi Domestic hot water tank temperature 	 ˚F

Air compressor – cut in 	 psi	cut out 	 psi Reduced 	 psi

6-6

BOILER ROOM LOG SHEET

Date 	 / 	 / 	 to 	 / 	 / 		STEAM 	 HOT WATER

SERVICE	BOILER ROOM NUMBER

DAILY	M	T	W T	F M T	W T	F M T	W T	F M	T W T	F

- Test try cocks *

- Test low water cut-offs *

- Blow down water columns *

- Blow down boilers (*)

- Service rotary cup burners

- Check burner operation

- Check all gauge readings

- Stick fuel oil tank

- Check unit ventilators

WEEKLY

- Test safety valves *

- Test scanners

- Test low draft cut-offs

- Service air compressor

- Drain compressor tank

- Clean oil strainers #

- Check expansion tanks

MONTHLY

- Clean boilers @	1 		2		3		4

- Service equipment and record on service sheets

- Flush condensate tanks *

- Flush hot water boilers

- Test relief valves

- Clean boiler room

*  Steam systems only (*)  See W.T. Specialist #   Heavy fuel oil only

@   PEOs only

6-7

| SECTION 7 BUILDING SERVICE STANDARDS |  |  |
| --- | --- | --- |
| The frequency of specific cleaning tasks has been itemized in the MCPS Procedures Manual. A copy of chapter five follows and items requiring special attention are highlighted. |  |  |
| The work of the building service staff consists of many tasks. The sum of these tasks, when properly carried out, should result in all areas of the building and grounds being adequately cared for. The Routine Task/Work Performance Guides on the following pages establish the frequencies for |  |  |
| conferences with personnel performing and supervising cleaning tasks. Any major variations from the standards should be brought to the attention of the building service supervisor, who will investigate the matter and make recommendations for action that should be taken to resolve the problem. |  |  |
| Items that have been added to the standard Building Service Standard Checklist as found in the MCPS Procedures Manual, are listed in a separate chart at the bottom of each page with recommended frequencies indicated with an ‘REC’. Changes to the frequencies of tasks on the standard checklist are indicated with a ‘REC’. |  |  |
| KEY FOR TASK/WORK PERFORMANCE GUIDE FREQUENCY |  |  |
| D DAILY W WEEKLY |  |  |
| M MONTHLY |  |  |
| Q QUARTERLY |  |  |
| A ANNUALLY |  |  |
| R AS REQUIRED |  |  |
|  |  | Page |
| Stairway Care |  | 7-3 |
| Office, Lounge, and Health Room Care |  | 7-4 |
| Classroom Cleaning | 7-5 |  |
| Restroom Cleaning and Service |  | 7-6 |
| Kitchen and Cafeteria Services |  | 7-7 |
| Outdoor and Grounds Care |  | 7-8 |
| Gymnasium Care |  | 7-9 |
| 7-1 |  |  |

CORRIDOR AND ENTRANCE CARE

Includes sweeping the corridors and entrance areas; removing all loose paper, trash, and rubbish; removing gum, tar, and other sticky substances from the floors; keeping trash receptacles emptied and presentable; cleaning drinking fountains and glass surfaces in the area; mopping up wet spots due to bad weather, leaks, or spills; keeping floor mats clean; and the proper care and maintenance of equipment and materials used. When floors are wet or slippery, keep warning signs in place.

| DUTIES | D | W | M | Q | A | R |
| --- | --- | --- | --- | --- | --- | --- |
| Dust horizontal surfaces | X |  |  |  |  |  |
| Dust mop floors & steps | X |  |  |  |  |  |
| Secure windows & doors | X |  |  |  |  |  |
| Wash fountains & fittings | X |  |  |  |  |  |
| Wash windows |  |  |  |  |  | X |
| Wash doors, frames, & glass |  |  |  |  |  | X |
| Wash entrance doors & glass | X |  |  |  |  |  |
| Wash lockers |  |  | X |  |  | X |
| Wash woodwork & trim |  |  |  |  |  | X |
| Wash lights and fixtures |  |  | REC |  |  | X |
| Dust walls & ceiling corners |  | X |  |  |  |  |
| Damp wipe exit lights & clocks |  |  | X |  |  |  |
| Damp wipe walls |  |  | X |  |  | X |
| Clean exhibit cases & art work |  | X |  |  |  |  |
| Clean/vacuum walk-off mats | X |  |  |  |  |  |
| Spot mop floors | X |  |  |  |  |  |
| Spray buff floors |  | X |  |  |  |  |
| Scrub or strip floors |  |  |  |  |  | X |
| Refinish floors |  |  |  |  |  | X |

| Wash interior window sills |  |  | REC |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Wash window troughs |  |  | REC |  |  |  |  |
| Wash steps & handrails |  | REC |  |  |  |  |  |
| Clean supply & return grills |  |  |  | REC |  |  |  |
| 7-2 |  |  |  |  |  |  |  |

STAIRWAY CARE

Includes all cleaning work inside the confines of the stairwells such as sweeping stair landings and steps; removal of gum or other foreign substances; dusting stair railings, clean glass, fire extinguisher, doors, ledges, etc.; cleaning and polishing handrails; wall spot cleaning; mopping or scrubbing stair landings and steps, thoroughly drying all water from these areas after mopping or scrubbing; and proper care and maintenance of stair cleaning equipment. The stairwell must be properly lighted.

| DUTIES | D | W | M | Q | A | R |
| --- | --- | --- | --- | --- | --- | --- |
| Dust horizontal surfaces | X |  |  |  |  |  |
| Dust mop steps & landings | X |  |  |  |  |  |
| Secure windows | X |  |  |  |  |  |
| Wash windows |  |  |  |  |  | X |
| Wash doors, frames, & glass |  |  |  |  |  | X |
| Wash stair treads |  | X |  |  |  |  |
| Wash stair risers |  |  |  |  |  | X |
| Wash lights and fixtures |  |  |  |  | X |  |
| Damp wipe handrails |  | X |  |  |  |  |
| Damp wipe walls |  |  | X |  |  | X |
| Damp wipe exit lights |  |  | X |  |  |  |
| Dust walls & ceiling corners |  |  | X |  |  |  |
| Replace light tubes/bulbs |  |  |  |  |  | X |
| Remove chewing gum |  |  |  |  |  | X |
| Remove graffiti |  |  |  |  |  | X |
| Wet mop landings |  | X |  |  |  |  |
| Scrub or strip landings |  |  |  |  |  | X |
| Refinish landings |  |  |  |  |  | X |

| Wash interior window sills |  |  | REC |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Wash window troughs |  |  | REC |  |  |  |
| Clean supply & return grills |  |  |  | REC |  |  |

7-3

OFFICE, LOUNGE, AND HEALTH ROOM CARE

Includes emptying wastebaskets; damp-wiping or dusting desks, counter tops, tables, filing cabinets, and other specified surfaces; cleaning sinks and toilets; sweeping or mopping floors and vacuuming carpet; scrubbing, stripping, refinishing, and buffing floors; proper care and maintenance of equipment and materials.

| DUTIES | D | W | M | Q | A | R |
| --- | --- | --- | --- | --- | --- | --- |
| Dust desks, tables, & chairs | X |  |  |  |  |  |
| Dust filing cabinets | X |  |  |  |  |  |
| Dust open book shelves |  | X |  |  |  |  |
| Dust telephones | X |  |  |  |  |  |
| Dust walls & ceiling corners |  |  | X |  |  |  |
| Dust mop floors | X |  |  |  |  |  |
| Vacuum carpet/rugs | X |  |  |  |  |  |
| Empty wastebaskets | X |  |  |  |  |  |
| Damp wipe telephones |  | X |  |  |  |  |
| Damp wipe clock |  |  | X |  |  |  |
| Wash windows |  |  | X |  |  |  |
| Wash door glass | X |  |  |  |  |  |
| Wash doors & frames |  | X |  |  |  |  |
| Wash woodwork & trim |  | X |  |  |  |  |
| Wash walls |  |  |  |  |  | X |
| Wash lights & fixtures |  |  |  |  | X | X |
| Clean shades/drapes |  |  | X |  |  |  |
| Adjust shapes/drapes uniformly | X |  |  |  |  |  |
| Secure windows & doors | X |  |  |  |  |  |
| Wet mop or spray buff floors |  | X |  |  |  |  |
| Scrub/strip & refinish floors |  |  |  |  |  | X |

| Wash interior window sills |  |  | REC |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Wash window troughs |  |  | REC |  |  |  |  |
| Clean supply & return grills |  |  |  | REC |  |  |  |
| Intensively clean carpets |  |  |  |  | REC |  |  |
| 7-4 |  |  |  |  |  |  |  |

CLASSROOM CLEANING

Includes emptying pencil sharpeners and wastebaskets; cleaning chalkboards and chalk trays; damp wiping or dusting desks, tables, cabinets, and other specified surfaces; cleaning student cloak closets, sinks, and toilets in assigned work area; sweeping or mopping floors; vacuuming carpet; securing windows; adjusting venetian blinds and drapes uniformly.

| DUTIES | D | W | M | Q | A | R |
| --- | --- | --- | --- | --- | --- | --- |
| Dust horizontal surfaces | X |  |  |  |  |  |
| Dust mop floors | X |  |  |  |  |  |
| Empty pencil sharpeners | X |  |  |  |  |  |
| Empty wastebaskets | X |  |  |  |  |  |
| Secure windows | X |  |  |  |  |  |
| Adjust blinds/drapes uniformly | X |  |  |  |  |  |
| Wash sink & fittings | X |  |  |  |  |  |
| Wash windows |  |  |  | X |  | X |
| Wash woodwork & trim |  |  |  |  |  | X |
| Wash doors & frames |  |  |  |  |  | X |
| Wash baseboards |  |  |  | X |  |  |
| Wash furniture |  |  |  | X |  |  |
| Wash lights & fixtures |  |  |  |  | X |  |
| Clean chalkboards & trays |  | X |  |  |  | X |
| Clean venetian blinds |  |  | X |  |  |  |
| Dust walls & ceiling corners |  |  |  | X |  |  |
| Vacuum carpet/rugs | X |  |  |  |  |  |
| Damp wipe clock, TV, computer monitors |  |  | X |  |  |  |
| Replace light tubes |  |  |  |  |  | X |
| Wet mop &/or spray buff floor |  |  |  |  |  | X |
| Scrub/strip & refinish floors |  |  |  |  |  | X |

| Wash interior window sills |  | REC |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Wash window troughs |  | REC |  |  |  |  |  |
| Clean supply & return grills |  |  |  | REC |  |  |  |
| Intensively clean carpet |  |  |  |  | 2REC |  |  |
| 7-5 |  |  |  |  |  |  |  |

RESTROOM CLEANING AND SERVICE

Includes all cleaning work inside restrooms such as: emptying waste receptacles; dusting window sills and ledges; cleaning walls, grills, mirrors, shelves, dispensers, waste receptacles, stall partitions and doors, wash basins, commodes, urinals, and polishing metal work; sweeping, mopping, or scrubbing floor; servicing toilet tissue, paper towel, sanitary napkin, soap dispensers; and the proper care and maintenance of restroom cleaning equipment.

| DUTIES | D | W | M | Q | A | R |
| --- | --- | --- | --- | --- | --- | --- |
| Dust horizontal surfaces | X |  |  |  |  |  |
| Wash sinks/basins & fittings | X |  |  |  |  |  |
| Wash urinals & fittings | X |  |  |  |  |  |
| Wash commodes including seats | X |  |  |  |  |  |
| Wash windows |  |  | X |  |  |  |
| Wash walls & ceiling |  |  |  |  | X | X |
| Wash lights & fixtures |  |  |  |  | X |  |
| Damp wipe partitions & walls |  | X |  |  |  | X |
| Polish metal work |  | X |  |  |  |  |
| Clean mirrors | X |  |  |  |  |  |
| Empty waste receptacles | X |  |  |  |  |  |
| Fill toilet tissue dispenser | X |  |  |  |  |  |
| Fill paper towel dispenser | X |  |  |  |  |  |
| Fill sanitary napkin dispenser | X |  |  |  |  |  |
| Clean and fill soap dispensers | X |  |  |  |  |  |
| Wet mop floor | X |  |  |  |  |  |
| Secure windows | X |  |  |  |  |  |
| Replace light tubes |  |  |  |  |  | X |
| Scrub and strip floors |  |  | X |  |  | X |

| Wash interior window sills |  |  | REC |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Wash window troughs |  |  | REC |  |  |  |
| Clean supply & return grills |  |  |  | REC |  |  |

7-6

KITCHEN AND CAFETERIA SERVICES

Includes removing trash/garbage from the kitchen and dining areas; washing and sanitizing trash cans, compactor room and compactor; washing overhead hoods, ducts, and pipes; removing and washing range hood filters; cleaning refrigerator/walk-in box floors; washing walls, windows, doors and door frames; wet mopping the kitchen and dining area floors with a sanitizing solution; setting up tables before lunch; damp wiping tables and putting them away after lunch; and the proper care and maintenance of the cleaning equipment.

| DUTIES | D | W | M | Q | A | R |
| --- | --- | --- | --- | --- | --- | --- |
| Wash hoods, filters, ducts, etc. |  |  | X |  |  |  |
| Wash trash/garbage cans | X |  |  |  |  |  |
| Wash door sills | X |  |  |  |  |  |
| Wash doors & door frames |  |  | X |  |  | X |
| Wash windows |  |  | X |  |  | X |
| Wash walls, woodwork, & trim |  |  |  | X |  | X |
| Wash lights & fixtures |  |  |  | X |  |  |
| Clean venetian blinds |  |  | X |  |  |  |
| Clean grease traps |  |  |  |  | X | X |
| Dispose of trash/garbage | X |  |  |  |  |  |
| Sweep cafeteria floor | X |  |  |  |  |  |
| Wet mop cafeteria floor | X |  |  |  |  |  |
| Wet mop kitchen floor | X |  |  |  |  |  |
| Spot mop floors - due to spills |  |  |  |  |  | X |
| Clean drinking fountains | X |  |  |  |  |  |
| Replace light tubes |  |  |  |  |  | X |
| Secure windows & doors | X |  |  |  |  |  |
| Spray buff cafeteria floor |  | X |  |  |  |  |
| Scrub/strip and refinish floors |  |  |  |  |  | X |

| Wash interior window sills |  |  | REC |  |  | REC |
| --- | --- | --- | --- | --- | --- | --- |
| Wash window troughs |  |  | REC |  |  | REC |
| Clean supply & return grills |  |  |  | REC |  |  |

7-7

OUTDOOR AND GROUNDS CARE

Consists of keeping school grounds clear of trash, glass, leaves, and other debris; sweeping sidewalks, parking lots, and paved play areas; hosing down sidewalks, steps, and outside entrance areas; maintaining the lawn in a presentable condition by mowing grass, trimming around the building, sidewalks, fence lines, etc.; pulling weeds and trimming shrubbery as necessary. During the winter, removing snow and ice from sidewalks, entrances, bus loading and unloading areas, oil fill pipe and stick lines, fire hydrants; and sanding icy areas as required.

| DUTIES | D | W | M | Q | A | R |
| --- | --- | --- | --- | --- | --- | --- |
| Pick up trash & debris | X |  |  |  |  |  |
| Sweep entrances & sidewalks | X |  |  |  |  |  |
| Sweep play area pavement |  | X |  |  |  | X |
| Sweep parking lots & driveway |  | X |  |  |  | X |
| Remove graffiti | X |  |  |  |  |  |
| Check playground equipment | X |  |  |  |  |  |
| Rake grounds |  |  |  |  |  | X |
| Remove leaves |  |  |  |  |  | X |
| Clean storm drain grating |  | X |  |  |  | X |
| Clean roof drains |  |  | X |  |  |  |
| Inspect gutters & downspouts |  | X |  |  |  |  |
| Mow lawn (in season) |  | X |  |  |  | X |
| Trim around building & walks |  | X |  |  |  | X |
| Trim along fence lines |  | X |  |  |  | X |
| Pull weeds |  |  |  |  |  | X |
| Trim shrubbery |  |  |  |  |  | X |
| Remove ice & snow |  |  |  |  |  | X |
| Sand icy areas |  |  |  |  |  | X |
| Replace burnt out light bulbs |  |  |  |  |  | X |

7-8

GYMNASIUM CARE

Includes all cleaning and service work associated with the gymnasium and related equipment such as: dust mopping floors daily and before and after athletic events, spot mopping as necessary; cleaning trash and debris from under and around bleachers; emptying trash receptacles; washing walls, doors, door frames, windows, and bleachers; making sure that bleachers, partition operators, basketball backboard operators, etc. are in good and safe working order; replacing light bulbs/tubes as necessary.

| DUTIES | D | W | M | Q | A | R |
| --- | --- | --- | --- | --- | --- | --- |
| Dust mop floors | X |  |  |  |  | X |
| Spot mop floors |  |  |  |  |  | X |
| Dust walls and bleachers |  |  | X |  |  |  |
| Wash walls and bleachers |  |  |  | X |  | X |
| Wash doors and door frames |  | X |  |  |  |  |
| Wash door glass | X |  |  |  |  |  |
| Empty trash receptacles | X |  |  |  |  |  |
| Clean under bleachers |  | X |  |  |  |  |
| Perform bleacher safety checks |  |  | X |  |  |  |
| Check partition operators |  | X |  |  |  |  |
| Check backboard operators |  | X |  |  |  |  |
| Check volleyball pole anchors | X |  |  |  |  |  |
| Replace burned out light bulbs |  |  |  |  |  | X |
| Remove gum/tar from floor |  |  |  |  |  | X |
| Remove graffiti |  |  |  |  |  | X |
| Wash windows |  |  |  | X |  |  |
| Wash light fixtures |  |  |  |  | X |  |
| Secure windows and doors | X |  |  |  |  |  |
| Scrub and refinish floors |  |  |  |  | X | X |

| Clean supply & return grills |  |  |  | REC |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Wash interior window sills |  |  |  | REC |  |  |
| Wash window troughs |  |  |  | REC |  |  |

7-9

SECTION 8	OTHER MAINTENANCE DUTIES

This section covers information on proper procedures for other duties such as ceiling tile replacement and carpet cleaning.

Page

Ceiling Tile Replacement Procedures	8-2

Carpet Care	8-3

8-1

CEILING TILE REPLACEMENT PROCEDURES

The following procedure should be used to replace moisture-damaged tiles after the source of water has been contained.

- Identify tiles with moisture staining and possible mold growth that need to be replaced.

- Check asbestos management plan to determine whether tile contains asbestos. If it does, removal should only be performed by trained and licensed asbestos workers. Contact Mr. Brown (301-670- 8238).

- Obtain appropriate replacement tiles.

- Prepare to do the replacement after school. Obtain the following before proceeding: replacement tile

vacuum cleaner

labeled spritzer bottle containing water ladder of appropriate height

utility knife, if necessary

face-fitting dust mask (recommended) heavy plastic trash bag

masking or duct tape

- Move furniture and other objects from the immediate vicinity of the work and cover other items to prevent debris from falling on these items.

- Cautiously lift an adjacent tile.

- Spray the backside (top side) of the tile to be removed with water to dampen any fine material resting on the tile

- Remove the tile from the grid and avoid tilting it and spilling debris.

- Place the tile directly into the garbage bag. Do not exceed the working limit of the bag.

- Install the new tile

- Remove equipment from the area and vacuum debris. Replace any moved objects.

8-2

Carpet Care

Carpeted areas can be separated into two broad categories according to use.

Medium Traffic—conference rooms, offices, media center, lounge

Heavy Traffic---Classrooms

Medium Traffic areas should be intensively cleaned on a yearly basis in addition to regular vacuuming. Heavy use areas should be intensively cleaned two times a year in addition to daily vacuuming.

The following guidelines should be followed when performing intensive carpet cleaning:

- Use an extraction vacuum for shampoo cleaning when available

- Bonnet cleaning may be used with a minimum of water when treating high traffic areas and/or areas of extreme staining

- Use only minimum amount of water for job

- Perform shampooing during daylight hours, Monday through Friday

- Ensure ventilation system is on during operation (7 a.m. to 7 p.m.). Contact Energy Management if under EM control (301-230-5482)

- Use dehumidifiers on a 24-hour basis as appropriate. Empty pans frequently.

- Keep lights on for 24-hour period.

- Keep blinds open during daytime hours.

- Where possible, keep hallway doors open.

8-3

APPENDIX A	REQUESTED MAINTENANCE SERVICES

This section covers the procedures and forms used to request maintenance services from the Division of Maintenance. Included is also a copy of outstanding work orders. The first set is dated at the approximate time of the creation of this BMP. Updated outstanding work orders should be requested from Division of Maintenance on a quarterly basis.

Page

Procedure for Requesting Maintenance Services	A-2

Record of Maintenance Services	A-3

A-1

Procedure for Requesting Maintenance Services

The building service manager is responsible for assessing any problems or needs relating to the school building, its equipment, or grounds, and making a determination as to whether the building services staff can handle the situation, or whether the services of the maintenance division will be required.

If maintenance services are required, the building service manager must submit a work order to the Division of Maintenance via the computerized work order system.

A-2

Record of Maintenance Services

Copies of work orders submitted for ventilation or indoor environmental quality-related repairs should be inserted here.

A-3

APPENDIX B	SAFETY & ENVIRONMENTAL GUIDELINES AND RECOMMENDATIONS

Montgomery County Public Schools (MCPS) is committed to providing a safe and healthful environment in support of the Success for Every Student Plan. Therefore, the following information is provided to reduce the risk of injury and the risk of environmental factors, which can adversely affect the quality of the learning environment.

The State of Maryland, which has adopted federal occupational safety and health regulations promulgated by the Occupational Safety and Health Administration (OSHA), regulates MCPS. The state regulates MCPS through the Maryland Occupational Safety and Health (MOSH) plan within the Division of Labor and Industry. Applicable worker safety and health regulations can be found in 29 Code of Federal Regulations, Part 1910 (available at http://www.osha.gov). Questions related to worker safety and health should be directed to the Building Service Supervisor or the Safety Supervisor, Department of Facilities Management.

If you have any questions regarding a potentially “unsafe” or “unhealthful” condition, please contact your supervisor immediately to report your concern(s).

If you have any questions regarding the following information, an environmental safety coordinator can be contacted at 301-926-4409.

SUMMARY OF TOPICS COVERED IN THIS DOCUMENT:

Page

| A. TEMPERATURE AND RELATIVE HUMIDITY | B-1 |
| --- | --- |
| B. CARPET REMOVAL PROCEDURES | B-2 |
| D. CONFINED SPACE | B-5 |
| E. RIGHT-TO-KNOW (MSDSs) | B-6 |
| G. LADDERS | B-7 |
| H. SANITIZATION PROCEDURES | B-7 |

- TEACHER CHECKLIST	B-8

  - TEMPERATURE AND RELATIVE HUMIDITY

Temperature and relative humidity are significant in investigations of indoor air quality complaints. When temperatures or humidities are outside the comfort zone, complaints about poor indoor air quality or discomfort will increase. Students, teachers, and administrative staff tend to become less tolerant of odors and other indicators of “poor air quality” at elevated temperatures and extreme relative humidities (and also less tolerant of non-IAQ stressors such as noise and overcrowding).

B-1

Additionally, to minimize foot discomfort, the surface temperature of the floor should be between 65 – 84°F. The following American Society of Heating, Refrigerating, and Air Conditioning Engineers (ASHRAE) table represents optimum and acceptable temperature ranges for typical classroom environments:

| Season | Optimum Temperature | Temperature Range (90% satisfaction criterion) |
| --- | --- | --- |
| Winter | 71 F | 68 – 75 F |
| Summer | 76 F | 73 –79 F |

Other than clothing, there are no adjustments for season or sex (male/female) to the temperatures of this table. For infants, certain elderly people, and individuals that are physically disabled, the lower limits of this table should be avoided.

This table was derived from the ANSI/ASHRAE 55-1992 Thermal Environmental Conditions for Human Occupancy.

MCPS has adopted the Board of Education’s energy conservation guidelines for temperature, which is 70°F in the winter season and 76°F in the summer season. Media centers and computer labs have a 75°F criterion for the cooling season and 70°F for the heating season.

The American Conference of Governmental Industrial Hygienists recommend maintaining relative humidity in the occupied space below 60% throughout the year in their “Guidelines for the Assessment of Bioaerosols in the Indoor Environment.” Humidity levels that exceed 60% will present a significant problem related to the potential for increased microbial growth. Based on the ANSI/ASHRAE 55-1992 Thermal Environmental Conditions for Human Occupancy guidelines, the relative humidity levels should be in the ranges listed below:

| Season | Relative Humidity Range |
| --- | --- |
| Winter | 25 – 60% |
| Summer | 20 – 60% |

  - CARPET REMOVAL PROCEDURES

Maintenance of carpet as recommended in the above section should ensure a complete life cycle for carpet in all but the most extreme use cases. When carpet can no longer be returned to acceptable conditions and represents an unacceptable risk to the quality of the indoor air environment, the following procedures should be strictly adhered to: (Note: This procedure should only be performed during non- occupied periods.)

B-2

- Day One Activities

  - Determine work area.

  - Turn off local unit ventilators in work area.

  - Wipe all removable items using damp cloth.

  - Remove wiped down items from the work area.

  - Place HEPA negative air filtration machine(s) in the work area and turn the fan speed to “High”. Allow the HEPA negative air filtration machine to exhaust INSIDE THE WORK AREA.

  - Seal all supply and return vents and grills in the room with plastic.

    - Close door or otherwise seal off work area before beginning work. Staff only exit work area in emergency.

  - Dampen carpet with clean water. Use enough water to ensure that the carpet is wet throughout the pile.

    - Use portable sprayer.

    - Worker Protection—disposable coveralls, dust masks

  - Cut carpet into strips as it is removed from floor.

  - Place carpet strips into non-marked disposal bags (6 mil plastic).

    - Seal bags shut with duct tape.

    - Worker Protection—gloves, disposable coveralls, dust masks

  - Vacuum floor with HEPA vacuum.

- Worker Protection—disposable coveralls, dust masks

- Scrape floor in preparation for new floor tile, remove underlying floor tile if necessary. - Worker Protection—gloves, disposable coveralls, dust masks

12. Vacuum floor with HEPA vacuum again.

- Worker Protection—disposable gloves, dust masks 13. Wipe all equipment (negative air machine, scrappers, tools, etc.) with a detergent solution.

- Worker Protection-gloves, disposable coveralls, and dust masks

- Remove all worker protection (personal protective equipment) and dispose in a plastic bag (6 mil plastic). Seal plastic bag with duct tape. - Remove bags of debris from building and transport to disposal area.

16. ALLOW HEPA NEGATIVE AIR FILTRATION MACHINES TO CONTINUE TO OPERATE. DO NOT REMOVE PLASTIC FROM VENTS OR GRILLS AND INSURE WORK AREA REMAINS SEALED.

- Day Two Activities - HEPA vacuum all wall, shelf, and flooring surfaces.

- Worker Protection—disposable coveralls, dust masks

- CONTINUE TO OPERATE THE HEPA NEGATIVE AIR FILTRATION MACHINES THROUGH THIS PROCESS. DO NOT REMOVE PLASTIC FROM VENTS OR GRILLS AND ENSURE THE WORK AREA REMAINS SEALED. 2. Start tile process after HEPA air filtration machines has operated for approximately 12 hours

since completion of carpet removal. 3. Remove plastic from vents and work area boundaries.

B-3

- Reactivate local ventilation.

- Apply water-based tile adhesive and wait until the surface is tacky enough for proper tile installation.

  - Worker Protection-gloves and safety splash goggles.

- Install floor tile.

- Damp mop completed tile floor and wax (3 coats).

- The HEPA negative air machines should remain operating to facilitate the new floor drying process.

- Start replacing furniture/materials in the work area.

  - LOCK-OUT/TAG-OUT

When employees are working on a piece of equipment (electrical, moving parts, energized systems, etc.) it must be locked out. Employees who are cleaning or performing maintenance where a body part could be injured should be using a “lock out tag out system”. The lock out system will physically stop the piece of machinery and render it safe. A tag is attached to notify other fellow employees that someone is working on the equipment and not to start it up. State occupational safety and health laws require these procedures be performed in accordance with a written Hazardous Energy Control Program.

All employees shall have their own locks and keys and they should be the only authorized individuals with access to their keys. No one else should be removing the lock except for the employee who attached it in the beginning of his/her maintenance work. After the lock is in place, try to start the machinery/equipment to ensure the right circuit has been disabled. At this time the employee is testing to ensure the circuit is not live and releasing any stored energy left in the system.

See your supervisor for additional information on “lock out tag out equipment” and proper use. If your facility has a Building Maintenance Plan, the site-specific lock out tag out procedures can be found in SECTION 2. For additional clarification, the following checklist is provided and lists the common questions to ask when performing lock-out/tag-out procedures:

| Yes/No | Item to be answered |
| --- | --- |
|  | Is the equipment you are working on capable of being turned off? |
|  | With the switch in the off or closed position, can you physically place a lock in to keep it from turning back on? |
|  | If the switch can not accept a lock can you disconnect power at the circuit board? |
|  | Make sure the lock you place is your lock issued to you and that you have the only key. |
|  | Did you attempt to turn the equipment on to release all stored energy? |
|  | Has normal movement completely stopped? |

B-4

  - CONFINED SPACE

The employee must be aware of hazards that he/she is completing as a result of the Building Maintenance Plan. Inspecting and cleaning the boilers present physical hazards to the employee. A boiler is commonly referred to as a pressurized vessel. It is also considered a confined space. It is large enough and so configured that an employee can bodily enter it, has a limited number of entrances and exits from the space, and was not built for humans to occupy the space. This is a requirement under federal OSHA, and State (MOSH).

The confined space may hold a build up of toxic gases or pockets where the oxygen level is too low for a human to be in there. An employee should not be entering into the boilers unless they have had prior intensive training. Employees who work or enter into confined spaces require special training and equipment.

If you have any questions as to whether something is a confined space or are unsure of the meaning of a confined space, please see your supervisor for further information. The following questions are provided to assist in determining if this applies to a given task:

| Yes/No | Item to be answered |
| --- | --- |
|  | Is it a confined space? - Large enough and so configured that an employee can enter, AND - Has limited entry or exit, AND - not designed for continuous occupancy? |
|  | Does the confined space contain corrosives or hazardous substances (acids, caustics) |
|  | Does the confined space have moving parts and equipment? |
|  | Are there areas not being ventilated in the space prior to entry? |
|  | Has testing shown that the area is oxygen deficient or has hazardous concentrations of potential contaminants, or that there is reason to believe that these conditions exist? |
|  | Are hazardous materials or gases being brought into the confined space by the worker? |
|  | Is it probable that portable electrical equipment used inside the area may not be grounded and insulated? |
|  | While in the area, are there decaying vegetation or animal matter observed? |

### IF YOU HAVE ANSWERED “YES” TO ANY QUESTION IN THIS SECTION OR SEE A ‘CONFINED SPACE’ LABEL ON ANY EQUIPMENT OR SPACE, DO NOT GO INTO THE SPACE. CONTACT YOUR SUPERVISOR IMMEDIATELY AND EXPLAIN THE SITUATION.

B-5

  - RIGHT-TO-KNOW (CILs and MSDSs)-- Access to Information About Hazardous and Toxic Substances:

The employee has the right to know what type of chemicals they are working with. The employee is also able to obtain chemical information that would be deemed pertinent information to the individual (i.e. health risks, health effects, reactivity, etc). Please remember that chemicals are not allowed to be purchased outright. The chemicals need to be procured. Employees need to purchase chemicals from the procurement list. This will ensure each chemical has been reviewed for safety and health affects before it enters the school system.

| Yes/No | Item to be answered |
| --- | --- |
|  | Is there a list of hazardous substances used in the facility? |
|  | Is each container for a hazardous substance (i.e. spray bottles, temporary bottles) labeled with product identity and warning information? |
|  | Has the employees supervisor reviewed with the employee the hazards (if any) associated with the product? |
|  | Does the employee know what to do if they are exposed to the hazardous substance? |

### IF YOU HAVE ANSWERED “NO” TO ANY QUESTION IN THIS SECTION CONTACT YOUR SUPERVISOR IMMEDIATELY AND EXPLAIN THE SITUATION.

  - WALKING/WORKING SURFACES

The employee must pay particular attention to hazards that are created by other work practices. Places in the facility that have a high traffic volume of people should be clean on a more frequent schedule. There is a significant reduction in occupational injuries with walking, working surfaces, and storage that is kept properly.

The following checklist provides questions to keep in mind while performing your normal duties:

| Yes/No | Item to be answered |
| --- | --- |
|  | Is the walking surface kept dry and free of debris? |
|  | Are spills of liquids cleaned up immediately and appropriately? |
|  | Does the facility have storage in a hap-hazard manner? |
|  | Are floors and carpets swept and vacuumed on a routine basis? |
|  | Are unused portions of service pits covered/protected by a guardrail? |

B-6

  - LADDERS

Ladders should be inspected on a frequent basis. If a ladder is found to be defective, the employee should take the ladder out of service and notify his or her supervisor. A tag should be attached to the ladder that states “Do Not Use – Danger”

Great care should be taken when placing ladders so that they are not carried or positioned near overhead power lines. Maintain at least ten-foot distance from over-head lines.

To ensure a safe ladder angle, the 4 to 1rule should always be obeyed. This rule states that the bottom of a leaning ladder is one foot away from the vertical surface being climbed for every four feet of working ladder length. Hence, the bottom of a ladder should be three feet from the wall when going up twelve feet of ladder length. Holding the ladder, placing the bottom of the ladder at one’s feet, and fully extending one’s arms generally achieves the proper angle.

The ladder should also extend three feet beyond the edge of the top of a wall when using the ladder to climb to the top of the wall.

  - SANITIZATION PROCEDURES

Due to certain circumstances sanitation of surfaces is recommended to remove noted or potential microbial contamination. The following are guidelines for ensuring successful results:

    - Remove all gross debris using a properly functioning commercial vacuum.

    - Prepare a detergent (such as A-125 or A-33) solution according to label instructions.	If a strong degreaser is needed, contact the Division of School Plant Operations for approved products.

    - Wash all non-porous surfaces, removing all residue.	Removal of residue is very important in ensuring decontamination and prevention of future contamination.

    - Wipe surfaces with clean water.

    - Allow surfaces to dry before reassembly (such as ventilation equipment).

B-7

  - TEACHER CHECKLIST (IAQ)

As indoor air quality (IAQ) can be strongly affected by occupant activities, in addition to the Tools For Schools checklists, building service or teacher staff may use the following checklist to ensure that conditions that promote poor indoor air quality can be avoided:

### INDOOR AIR QUALITY (IAQ) CLASSROOM CHECKLIST

Keep the wall unit ventilator in the “ON” position.

Keep papers, boxes, and other materials off of the unit ventilator vents.

Keep plants and other organic displays off the unit ventilator or hanging over the unit.

Keep desks, and other furniture at least 3-5 feet away from the front of the wall unit ventilator

Do not tape papers, posters, laminating material or any other material including “sticky” back shelves, or folders on the wall unit ventilator

Report any deficiencies (odors, noise, excessive temperature variations, leaks, visible mold, etc.) of the ventilation system (wall unit ventilators, ceiling units, etc) to your Building Service Manager or Plant Equipment Operator immediately.

Report water-damaged and stained ceiling tiles immediately to your Building Service Manager.

Only food items being used as part of the curriculum should be stored in the classroom and should be in air-tight containers.

Refer to the MCPS Safety Handbook for information on having animals in the classroom (Section 8-78, page 115).

Sightings of insects and/or rodents should be reported to your Building Service Manager immediately.

B-8

APPENDIX C	PM VISIT WORK PLANs

The following work plan was developed based on observations and measurements explained in the initial assessment described in Appendix E. The plan is broken into four categories, indicating the groups that have primary responsibility to complete the identified tasks. Target completion dates of these tasks are indicated.

Page

Primary Responsibility – IAQ Team	C-2

Primary Responsibility – Building Service Manager	C-3

Primary Responsibility – Maintenance	C-4

Primary Responsibility – Building Staff	C-5

| First Return Visit |  |
| --- | --- |
| Primary Responsibility – IAQ Team | C-6 |
| Primary Responsibility – Building Service Manager | C-7 |
| Primary Responsibility – Building Staff | C-8 |
| Second Return Visit |  |
| Primary Responsibility – IEQ Team | C-9 |
| Primary Responsibility – Building Service Manager | C-10 |
| Primary Responsibility – Building Staff | C-10 |
| C-1 |  |

Alpha Elementary Work Plan	2/25/00

IAQ Team

| PRIMARY RESPONSIBILITY | TASK | INITIATED | SCEHULED COMPLETION | ACTUAL COMPLETION |
| --- | --- | --- | --- | --- |
| IAQ Team | Clean, adjust, replace defective components in univents or other air handlers. Verify correct room control and fix if needed. Verify correct heat valve control and correct if leaking or otherwise dripping. Cleaning and disinfection should be thorough in each unit up to the outside air damper in univents and to the intake grill on other air handlers. Filter replacement if needed. Occupied rooms to be addressed are in the zones listed below. Zones are to be prioritized in the following order: 14, 13, 18, 17, 9, 16, 2, 6, 11, 12, 10, 7, |  |  | 12/23/99 |
| IAQ Team | Verify performance of relief device; advise. Occupied rooms to be addressed are in the zones listed below. Zones are to be prioritized in the following order: 14, 13, 18, 17, 9, 16, 2, 6, 11, 12, 10, 7 |  |  | 12/23/99 |
| IAQ Team | Additional tasks to complete are as follow: - Counselor’s office: correct draft problem at univent - Resource Room: fix filter holder in univent - Room 14: fix univent cover |  |  | 12/23/99 |
| IAQ Team | Clean univent intake chambers and inside of intake grills. |  | 7/1/00 |  |
| IAQ Team | Clean evaporator coils and drain pans in RTU’s 3, 4, 5, 6 | 12/23/99 | 7/1/00 |  |

C-2

Alpha Elementary Work Plan	2/25/00

Building Service Manager

| PRIMARY RESPONSIBILITY | TASK | INITIATED | SCEHULED COMPLETION | ACTUAL COMPLETION |
| --- | --- | --- | --- | --- |
| Building Service Manager | Replace ceiling tiles as needed after leaks have been corrected. IAQ Team will instruct. | 12/23/99 | 2/19/00 |  |
| Building Service Manager | Review carpet maintenance methods and schedule | 12/23/99 | 2/19/00 |  |
| Building Service Manager | Review dusting methods and schedules | 12/23/99 | 2/19/00 |  |
| Building Service Manager | Clean window troughs and interior sills with a phosphate detergent or suitable alternative. Establish a schedule to inspect troughs and sills and to clean those components | 12/23/99 | 2/19/00 |  |
| Building Service Manager | Clean ventilation terminal devices and establish a schedule for that action | 12/23/99 | 2/19/00 |  |
| Building Service Manager | Verify that all containers containing maintenance products (e.g. soap, polish, buffing solution, etc.) are labeled | 1/24/00 | 2/19/00 |  |
| Building Service Manager | Verify that all maintenance chemical products are district approved. Remove non-approved products from school grounds | 1/24/00 | 4/21/00 |  |
| Building Service Manager | Clear areas in front of electrical panels of debris, equipment, and other obstructions for at least 3 feet | 12/23/99 | 4/21/00 |  |
| Building Service Manager | Remove padlocks from roof-top AC unit switches | 12/23/99 | 4/21/00 |  |
| Building Service Manager | Notify IPM of on-going pest problems throughout the building. IPM should follow-up | 12/23/99 | 4/21/00 |  |

C-3

Alpha Elementary Work Plan	2/25/00

Maintenance

| PRIMARY RESPONSIBILITY | TASK | INITIATED | SCEHULED COMPLETION | ACTUAL COMPLETION |
| --- | --- | --- | --- | --- |
| Maintenance | Remove univentilator outside grilles. Fill exposed wall block cavities between grill and unit. Disinfect if needed. Replace grill with modified attachment to facilitate easy removal of grill in future. | 12/23/99 | 7/1/00 |  |
| Maintenance | Repair 3-way mixing valve that is leaking in boiler room | 12/23/99 | 7/1/00 |  |
| Maintenance | If possible install filter access doors in fan coils in resource room and math lab | 12/23/99 | 7/1/00 |  |
| Maintenance | Repack valve and replace thermostat (Johnson 4756-205) in room 22 | 12/23/99 | 7/1/00 |  |

C-4

Alpha Elementary Work Plan	2/25/00

Building Staff

| PRIMARY RESPONSIBILITY | TASK | INITIATED | SCEHULED COMPLETION | ACTUAL COMPLETION |
| --- | --- | --- | --- | --- |
| Building Staff | Remove books, papers and other items from the tops and sides of univentilators and keep clear. | 12/23/99 | 1/14/00 |  |
| Building Staff | Assign a person to create and maintain product inventory especially for maintenance, kitchen, science and art areas | 12/23/99 | 1/14/00 |  |
| Building Staff | Verify that all chemical products are district approved. Remove non- approved products from school grounds | 12/23/99 | 1/14/00 |  |
| Building Staff | Verify that all containers containing chemical products are labeled and kept closed | 12/23/99 | 1/14/00 |  |

C-5

Alpha ES 1st Return Visit Work Plan	6/28/01 IAQ Team

| PRIMARY RESPONSIBILITY | TASK | INITIATED | SCEHULED COMPLETION | ACTUAL COMPLETION |
| --- | --- | --- | --- | --- |
| IAQ Team | Verify accuracy and completeness of supply and exhaust equipment tables in building maintenance plan. | 7/30/01 |  | 9/7/01 |
| IAQ Team | Provide annual PM service to ventilation equipment as indicated in BMP. Record activities on individual service record pages for each piece of equipment. Indicate any non-routine work completed on equipment in the “comments” column of those pages. The predominant finding during the annual building assessment was low room temperatures. | 7/30/01 |  | 9/7/01 |
| IAQ Team | Verify roof labels are still legible. | 7/30/01 |  | 9/7/01 |
| IAQ Team | Check volumetric flow rates of six unit ventilators at random. Check volumetric flowerets of three restroom ceiling exhausts and three restroom wall exhausts. Try to locate ventilation equipment schedules to determine design flow rates. | 7/30/01 |  | 9/7/01 |

\

C-6

Alpha ES 1st Return Visit Work Plan	6/28/01 Building Service Manager

| PRIMARY RESPONSIBILITY | TASK | INITIATED | SCEHULED COMPLETION | ACTUAL COMPLETION |
| --- | --- | --- | --- | --- |
| Building Service Manager | It is critical that all ventilation equipment receive regular preventive maintenance as described in the building maintenance plan. Those maintenance activities should be recorded in the maintenance plan on individual service record pages. | 7/30/01 | 10/30/01 |  |
| Building Service Manager | Systematically inspect all areas for moldy ceiling tiles, sagging and/or broken ceiling tile grids, and missing ceiling tiles. Replace moldy ceiling tiles immediately using guidelines found in the building maintenance plan. Issue work orders for ceiling grid repairs. Replace missing ceiling tiles. | 7/30/01 | 10/30/01 |  |
| Building Service Manager | Continue to remove unapproved products from the school. Refer to the list of approved products. | 7/30/01 | 10/30/01 |  |
| Building Service Manager | Systematically survey all building service areas for unlabelled secondary containers. Place adequate labels on those items. | 7/30/01 | 10/30/01 |  |
| Building Service Manager | Continue to implement the area cleaning schedules as they are presented in the building maintenance plan. | 7/30/01 | 10/30/01 |  |

C-7

Alpha ES 1st Return Visit Work Plan	6//28/01 Building Staff

| PRIMARY RESPONSIBILITY | TASK | INITIATED | SCEHULED COMPLETION | ACTUAL COMPLETION |
| --- | --- | --- | --- | --- |
| Building Staff | Be vigilant about reporting problems with unit ventilators and air handlers to building services. Unit ventilators and air handlers need to operate during times of occupancy. | 7/30/01 | 10/30/01 |  |
| Building Staff | Continue to remove unapproved products from the building. Refer to the list of approved products. | 7/30/01 | 10/30/01 |  |
| Building Staff | Keep computers, TVs and furniture away from thermostats. | 7/30/01 | 10/30/01 |  |
| Building Staff | The success of this IAQ PM program is not only measured by the air sampling and observations made during the assessment, but also the response from building staff, in particular, their perception of the building’s indoor environmental quality. The questionnaires that the Team program uses are an important tool used to measure staff perceptions. Past response rates to questionnaires has been poor. We strongly suggest that the school administration announce their endorsement of the program and encourage staff participation, even if staff commonly believe there are no IAQ problems. | 7/30/01 | 10/30/01 |  |

C-8

Alpha ES Return Visit 2 Work Plan	09/27/04 Items to be completed by IAQ Team

- Verify accuracy and completeness of supply and exhaust equipment information in building

maintenance plan. Special emphasis on electrical information.

- Record all thermostat temperature settings and air temperatures at stats before work commences (Pre). After PM work is completed, record stat settings and air temperatures (Post).

- Before PM cleaning or HVAC work is performed - Record volumetric flow rates of six unit ventilators at random. Record volumetric flow rates of three restroom ceiling exhausts. Record volumetric flow rates from all supply and return devices in the main office suite and rooms K1/K2.

- Provide annual Preventive Maintenance (PM) service to ventilation units: HEPA vacuum interior, replace filters as needed, repair damaged insulation, evaluate mechanical condition/operation and cleanliness, complete minor repairs, identify necessary major repairs. Record activities on individual service record pages for each piece of equipment. Note any cleaning and repair work completed on equipment. Also indicate total time and parts spent on repair work.

- Verify roof labels are still legible on ventilation equipment. Re-label if needed.

- Complete annual PM routines on all exhaust fans.

- Complete annual PM routine on the air station.

- The following special projects should be completed by the Team during this visit:

  - During the walkthrough, outdoor air dampers were fully closed in several univents. Verify proper operation of outdoor air dampers (determine if dampers are designed to close fully or to a minimum position). If necessary, determine feasible means for modifying univents to ensure continuous outdoor air supply.

  - Check all condensate drains penetrating exterior walls – extend any drains that are directing condensate against the walls.

  - Some univent condensate drain pans have been installed without the rear screws, resulting in poor drainage. Check (and correct) positioning of condensate drain pans in all univents – pans should be tilted to allow adequate drainage.

Items to be completed by Building Services

- Continue to systematically inspect all areas for moldy ceiling tiles, sagging and/or broken ceiling tile grids, missing ceiling tiles, and excessively stained ceiling tiles. Replace moldy ceiling tiles

immediately using guidelines found in the building maintenance plan. Replace missing, damaged, and stained ceiling tiles (replace water-stained tiles after leaks have been repaired).

- Remove unapproved products, if found, from the building. Refer to the list of MCPS approved products.

- Ensure that secondary containers, such as spray bottles and buckets, are labeled with labels that include the product name and hazard. Systematically survey all building service areas for unlabelled secondary containers. Place adequate labels on these items.

- Continue to be vigilant about regularly scheduled ventilation filter changes for all floor and ceiling univents and air handlers, and thoroughly implement the cleaning schedule as described in the building maintenance plan.

Items to be completed by Staff

- Be vigilant about reporting water leaks and problems with ventilation equipment to building services. Unit ventilators and air handlers need to operate during times of occupancy.

- Keep the top and bottom grilles of floor-mounted unit ventilators clear of books, papers, potted plants, furniture, and other obstructions.

- Ensure that thermostats are free of obstructions.

- Refer to the list of approved products prior to bringing items such as cleaning solutions, soaps, and air fresheners into the building. Remove unapproved products.

C-10

APPENDIX D	Indoor Environmental Quality (IEQ) Building Reports

This appendix contains the initial and final assessment performed at the time of the institution of this BMP. Any following indoor environmental quality reports and/or assessments should be included in this appendix in chronological order.

Page

Initial Assessment	D-2

Review of Supporting Documents	D-2

Summary Findings from Questionnaire and Interviews	D-3

Results of Initial Walk-through	D-3

Follow-up IEQ Assessments	D-5

D-1

In actual BMPs, site visit reports for all PM visits are inserted here.

D-2

APPENDIX E	TRAINING and INFORMATION

This appendix covers information required by the chemical inventory list and associated training requirements. Other required training documents are also in this appendix. Additionally, IAQ awareness training and the Tools for Schools action kit are included. All records for these training programs shall be kept in this appendix.

Page

Hazardous/Toxic Chemical Inventory List(s)	E-2 Hazcom Training Program for Alpha Elementary	E-3

Hazcom Training Record for Alpha Elementary	E-9 Staff Lock-out/Tag-out Training

Lock-out/Tag-out Training Program for Alpha Elementary	E-10

Lock-out/Tag-out Training Records for Alpha Elementary	E-14 Staff IAQ Awareness Training & Tools for Schools Introduction

IAQ Awareness Training Program	E-15

IAQ Awareness Training Records	E-24

*MCPS Approved Products List	E-25

(For Tools for Schools, please refer to the U.S. EPA Action Kit that is included with this Building Management Plan)

* Additional copies of the MCPS Approved Products List can be downloaded at: http://www.mcps.k12.md.us/departments/iaq/products.htm

E-1

In actual BMPs, copies of awareness training presentations and associated records are inserted here. Two hardcopies of the MCPS Approved Products List are also inserted.